# PicoPort BACnet PICS

BACnet Protocol Implementation Conformance Statement (PICS)

Date: 	December 11, 2020

Vendor Name: 	ICC, Inc.

Product Name:	PicoPort Communications Module

Product Model Number: 	PicoPort

Application Software Version:	V4.300

Firmware Revision:	V4.300

BACnet Protocol Revision:	12

Product Description:

The PicoPort is a miniature serial communications engine-on-module for OEM applications. This product supports native BACnet, connecting directly to the MS/TP LAN using baud rates of 9600, 19200, 38400, 57600, 76800, and 115200. The device can be configured as a BACnet Client or as a BACnet Server.

BACnet Standard Device Profile (Annex L):

BACnet Operator Workstation (B-OWS)

BACnet Building Controller (B-BC)

BACnet Advanced Application Controller (B-AAC)

BACnet Application Specific Controller (B-ASC)

BACnet Smart Sensor (B-SS)

BACnet Smart Actuator (B-SA)

BACnet Interoperability Building Blocks Supported (Annex K):

Data Sharing – ReadProperty-A (DS-RP-A)

Data Sharing – ReadProperty-B (DS-RP-B)

Data Sharing – ReadPropertyMultiple-B (DS-RPM-B)

Data Sharing – WriteProperty-A (DS-WP-A)

Data Sharing – WriteProperty-B (DS-WP-B)

Data Sharing – WritePropertyMultiple-B (DS-WPM-B)

Data Sharing – COV-B (DS-COV-B)

Device Management – Dynamic Device Binding-A (DM-DDB-A)

Device Management – Dynamic Device Binding-B (DM-DDB-B)

Device Management – Dynamic Object Binding-B (DM-DOB-B)

Device Management – DeviceCommunicationControl-B (DM-DCC-B)

Device Management – ReinitializeDevice-B (DM-RD-B)

Device Management – TimeSynchronization-B (DM-TS-B)*

Device Management – UTCTimeSynchronization-B (DM-UTC-B)*

* Available only when Real-time Clock Settings are enabled

Segmentation Capability:

Able to transmit segmented messages	Window Size ________

Able to receive segmented messages	Window Size ________

Standard Object Types Supported:

| Property | Object Type |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Device | Binary Input | Binary Output | Binary Value | Analog Input | Analog Output | Analog Value | Multi-state Input | Multi-state Output | Multi-state Value |
| Object Identifier | W | R | R | R | R | R | R | R | R | R |
| Object Name | W | R | R | R | R | R | R | R | R | R |
| Object Type | R | R | R | R | R | R | R | R | R | R |
| System Status | R |  |  |  |  |  |  |  |  |  |
| Vendor Name | R |  |  |  |  |  |  |  |  |  |
| Vendor Identifier | R |  |  |  |  |  |  |  |  |  |
| Model Name | R |  |  |  |  |  |  |  |  |  |
| Firmware Revision | R |  |  |  |  |  |  |  |  |  |
| Application Software Version | R |  |  |  |  |  |  |  |  |  |
| Protocol Version | R |  |  |  |  |  |  |  |  |  |
| Protocol Revision | R |  |  |  |  |  |  |  |  |  |
| Protocol Services Supported | R |  |  |  |  |  |  |  |  |  |
| Protocol Object Types Supported | R |  |  |  |  |  |  |  |  |  |
| Object List | R |  |  |  |  |  |  |  |  |  |
| Max APDU Length Accepted | R |  |  |  |  |  |  |  |  |  |
| Segmentation Supported | R |  |  |  |  |  |  |  |  |  |
| Local Time* | W |  |  |  |  |  |  |  |  |  |
| Local Date* | W |  |  |  |  |  |  |  |  |  |
| UTC Offset* | W (-840…720) |  |  |  |  |  |  |  |  |  |
| Daylight Savings Status* | W |  |  |  |  |  |  |  |  |  |
| APDU Timeout | W (10…65535) |  |  |  |  |  |  |  |  |  |
| Number Of APDU Retries | W (0…10) |  |  |  |  |  |  |  |  |  |
| Max Master | W (1…127) |  |  |  |  |  |  |  |  |  |
| Max Info Frames | W (1…100) |  |  |  |  |  |  |  |  |  |
| Device Address Binding | R |  |  |  |  |  |  |  |  |  |
| Database Revision | R |  |  |  |  |  |  |  |  |  |
| Active COV Subscriptions | R |  |  |  |  |  |  |  |  |  |
| Present Value |  | R | W | W | R | W | W | R | W | W |
| Status Flags |  | R | R | R | R | R | R | R | R | R |
| Event State |  | R | R | R | R | R | R | R | R | R |
| Reliability |  | R | R | R | R | R | R | R | R | R |
| Out Of Service |  | R | R | R | R | R | R | R | R | R |
| Number Of States |  |  |  |  |  |  |  | R | R | R |
| Units |  |  |  |  | R | R | R |  |  |  |
| Priority Array |  |  | R | R |  | R | R |  | R | R |
| Relinquish Default |  |  | R | R |  | R | R |  | R | R |
| COV Increment |  |  |  |  | W | W | W |  |  |  |
| Polarity |  | W | W |  |  |  |  |  |  |  |
| Inactive Text |  | R | R | R |  |  |  |  |  |  |
| Active Text |  | R | R | R |  |  |  |  |  |  |

R – Readable using BACnet services

W – Readable and writable using BACnet services

* Available only when Real-time Clock Settings are enabled

Data Link Layer Options:

BACnet IP, (Annex J)

BACnet IP, (Annex J), Foreign Device

ISO 8802-3, Ethernet (Clause 7)

ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)

ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ______

MS/TP master (Clause 9), baud rate(s):  9600, 19200, 38400, 57600, 76800, 115200

MS/TP slave (Clause 9), baud rate(s): ______

Point-To-Point, EIA 232 (Clause 10), baud rate(s): ______

Point-To-Point, modem, (Clause 10), baud rate(s): ______

LonTalk, (Clause 11), medium: ______

Other: ______

Device Address Binding:

Is static device binding supported? (This is currently for two-way communication with MS/TP slaves and certain other devices.)	 Yes    No

Networking Options:

Router, Clause 6 - List all routing configurations

Annex H, BACnet Tunneling Router over IP

BACnet/IP Broadcast Management Device (BBMD)

Does the BBMD support registrations by Foreign Devices? 	 Yes    No

Network Security Options:

Non-secure Device - is capable of operating without BACnet Network Security

Secure Device - is capable of using BACnet Network Security (NS-SD BIBB)

Multiple Application-Specific Keys:

Supports encryption (NS-ED BIBB)

Key Server (NS-KS BIBB)

Character Sets Supported:

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

ISO 10646 (UTF-8)		 IBM™/Microsoft™ DBCS	 JIS X 0208

ISO 10646 (UCS-4)	 ISO 10646 (UCS-2 )		 ISO 8859-1

If this product is a communication gateway, describe the types of non-BACnet equipment/networks(s) that the gateway supports:

Refer to protocol-specific manuals for other supported protocols.