## Toshiba Inverter Object Mapping
Object Mapping Table Instructions 1. Locate the Inverter Parameter Number column for your inverter type 2. Click the down arrow [▼] in the column header to show filter options 3. Uncheck the item titled "N/A" in the filter list 4. Click the OK button 5. Parameters for only your inverter type will be displayed | [7 empty] | * Refer to inverter's parameter number column for bit number | RED-485 Toshiba AS3 V1.2 | RED-485 Toshiba S15 V1.2 | RED-485 Toshiba NC3 V1.2 | RED-485 Toshiba AS1 V1.2 | RED-485 Toshiba 9-Series V1.2 | RED-485 Toshiba 7-Series V1.1
Parameter |  |  |  |  | Protocol Object |  |  |  | Inverter Parameter Number
Name | Type | Resolution | Units | Read/Write | BACnet Object | N2 Object | FLN Point | Modbus Register | AS3 | S15 | NC3 | AS1 | 9-Series | 7-Series
Output Frequency | Analog Input | 0.01 | Hz | R | AI1 | AI1 | 3 | 30001 / 40001 | FD00 | FD00 | FD00 | FD00 | FD00 | FD00
Frequency Reference | Analog Input | 0.01 | Hz | R | AI2 | AI2 | 4 | 30002 / 40002 | FD02 | FD02 | FD02 | FD02 | FD02 | FE02
Output Speed | Analog Input | 1 | RPM | R | AI3 | AI3 | 5 | 30003 / 40003 | FD90 | FD90 | N/A | FE90 | FE90 | N/A
Speed Reference | Analog Input | 1 | RPM | R | AI4 | AI4 | 6 | 30004 / 40004 | FD94 | N/A | N/A | N/A | N/A | N/A
Input Voltage | Analog Input | 0.01 | % | R | AI5 | AI5 | 7 | 30005 / 40005 | FD04 | FD04 | FD04 | FD04 | FD04 | FE04
Output Voltage | Analog Input | 0.01 | % | R | AI6 | AI6 | 8 | 30006 / 40006 | FD05 | FD05 | FD05 | FD05 | FD05 | FE05
Output Current | Analog Input | 0.01 | % | R | AI7 | AI7 | 9 | 30007 / 40007 | FD03 | FD03 | FD03 | FD03 | FD03 | FE03
Torque | Analog Input | 0.01 | % | R | AI8 | AI8 | 10 | 30008 / 40008 | FD18 | FD18 | FD18 | FD18 | FD18 | FE18
Input Power | Analog Input | 0.01 | KW | R | AI9 | AI9 | 11 | 30009 / 40009 | FD29 | FD29 | FD29 | FD29 | FD29 | FE29
Output Power | Analog Input | 0.01 | KW | R | AI10 | AI10 | 12 | 30010 / 40010 | FD30 | FD30 | FD30 | FD30 | FD30 | FE30
Input Energy | Analog Input | 1 | KWH | R | AI11 | AI11 | 13 | 30011 / 40011 | FE76 | FE76 | N/A | FE76 | FE76 | N/A
Output Energy | Analog Input | 1 | KWH | R | AI12 | AI12 | 14 | 30012 / 40012 | FE77 | FE77 | N/A | FE77 | FE77 | N/A
Motor Load | Analog Input | 1 | % | R | AI13 | AI13 | 15 | 30013 / 40013 | FD26 | FD26 | FD26 | FD26 | FD26 | FE26
ASD Load | Analog Input | 1 | % | R | AI14 | AI14 | 16 | 30014 / 40014 | FD27 | FD27 | FD27 | FD27 | FD27 | FE27
Run Time | Analog Input | 1 | Hours | R | AI15 | AI15 | 17 | 30015 / 40015 | FE14 | FE14 | FE14 | FE14 | FE14 | FE14
Fault Code | Analog Input | 1 |  | R | AI16 | AI16 | 18 | 30016 / 40016 | FC90 | FC90 | FC90 | FC90 | FC90 | FC90
Last Fault 1 | Analog Input | 1 |  | R | AI17 | AI17 | 19 | 30017 / 40017 | FE10 | FE10 | FE10 | FE10 | FE10 | FE10
Last Fault 2 | Analog Input | 1 |  | R | AI18 | AI18 | 21 | 30018 / 40018 | FE11 | FE11 | FE11 | FE11 | FE11 | FE11
Alarm Info | Analog Input | 1 |  | R | AI19 | AI19 | 22 | 30019 / 40019 | N/A | N/A | N/A | N/A | N/A | FC91
Alarm Info 1 | Analog Input | 1 |  | R | AI19 | AI19 | 22 | 30019 / 40019 | FC91 | FC91 | FC91 | FC91 | FC91 | N/A
Alarm Info 2 | Analog Input | 1 |  | R | AI20 | AI20 | 23 | 30020 / 40020 | FC92 | FC92 | FC92 | FC92 | FC92 | N/A
RR Terminal | Analog Input | 0.01 | % | R | AI21 | AI21 | 24 | 30021 / 40021 | FE35 | N/A | N/A | FE35 | FE35 | FE35
RX Terminal | Analog Input | 0.01 | % | R | AI22 | AI22 | 25 | 30022 / 40022 | FE36 | N/A | N/A | FE37 | FE37 | FE37
II Terminal | Analog Input | 0.01 | % | R | AI23 | AI23 | 26 | 30023 / 40023 | FE37 | N/A | N/A | N/A | N/A | N/A
VI Terminal | Analog Input | 0.01 | % | R | AI21 | AI21 | 24 | 30021 / 40021 | N/A | N/A | FE35 | N/A | N/A | N/A
VI/II Terminal | Analog Input | 0.01 | % | R | AI23 | AI23 | 26 | 30023 / 40023 | N/A | N/A | N/A | FE36 | N/A | FE36
V/I Terminal | Analog Input | 0.01 | % | R | AI23 | AI23 | 26 | 30023 / 40023 | N/A | N/A | N/A | N/A | FE36 | N/A
VIA Terminal | Analog Input | 0.01 | % | R | AI21 | AI21 | 24 | 30021 / 40021 | N/A | FE35 | N/A | N/A | N/A | N/A
VIB Terminal | Analog Input | 0.01 | % | R | AI22 | AI22 | 25 | 30022 / 40022 | N/A | FE36 | N/A | N/A | N/A | N/A
VIC Terminal | Analog Input | 0.01 | % | R | AI23 | AI23 | 26 | 30023 / 40023 | N/A | FE37 | N/A | N/A | N/A | N/A
FM Terminal | Analog Input | 0.01 | % | R | AI24 | AI24 | 27 | 30024 / 40024 | FE40 | FE40 | N/A | FE40 | FE40 | FE39
AM Terminal | Analog Input | 0.01 | % | R | AI25 | AI25 | 28 | 30025 / 40025 | FE41 | N/A | N/A | FE41 | FE41 | FE40
Input Voltage (V) | Analog Input | 0.01 | Volts | R | AI26 | AI26 | 95 | 30031 / 40031 | FD04 x FE71 | FD04 x FE71 | FD04 x FE71 | FD04 x FE71 x √2 | FD04 x FE71 x √2 | N/A
Output Voltage (V) | Analog Input | 0.01 | Volts | R | AI27 | AI27 | 96 | 30032 / 40032 | FD05 x FE71 | FD05 x FE71 | FD05 x FE71 | FD05 x FE71 | FD05 x FE71 | N/A
Output Current (A) | Analog Input | 0.01 | Amps | R | AI28 | AI28 | 97 | 30033 / 40033 | FD03 x FE70 | FD03 x FE70 | FD03 x FE70 | FD03 x FE70 | FD03 x FE70 | N/A
Run/Stop | Digital Input |  |  | R | BI1 | BI1 | 30 | 30026 / 40026 Bit 10 | FD01 Bit 10 | FD01 Bit 10 | FD01 Bit 10 | FD01 Bit 10 | FD01 Bit 10 | FE01 Bit 10
Forward/Reverse | Digital Input |  |  | R | BI2 | BI2 | 31 | 30026 / 40026 Bit 9 | FD01 Bit 9 | FD01 Bit 9 | FD01 Bit 9 | FD01 Bit 9 | FD01 Bit 9 | FE01 Bit 9
Fault Status | Digital Input |  |  | R | BI3 | BI3 | 32 | 30026 / 40026 Bit 1 | FD01 Bit 1 | FD01 Bit 1 | FD01 Bit 1 | FD01 Bit 1 | FD01 Bit 1 | FC90 != 0
Alarm Status | Digital Input |  |  | R | BI4 | BI4 | 33 | 30026 / 40026 Bit 2 | FD01 Bit 2 | FD01 Bit 2 | FD01 Bit 2 | FD01 Bit 2 | FD01 Bit 2 | FC91 != 0
DC Braking | Digital Input |  |  | R | BI5 | BI5 | 34 | 30026 / 40026 Bit 7 | FD01 Bit 7 | FD01 Bit 7 | FD01 Bit 7 | FD01 Bit 7 | FD01 Bit 7 | FE01 Bit 7
Jog Run | Digital Input |  |  | R | BI6 | BI6 | 35 | 30026 / 40026 Bit 8 | FD01 Bit 8 | FD01 Bit 8 | FD01 Bit 8 | FD01 Bit 8 | FD01 Bit 8 | FE01 Bit 8
Coast Stop | Digital Input |  |  | R | BI7 | BI7 | 36 | 30026 / 40026 Bit 11 | FD01 Bit 11 | FD01 Bit 11 | FD01 Bit 11 | FD01 Bit 11 | FD01 Bit 11 | N/A
Emergency Stop | Digital Input |  |  | R | BI8 | BI8 | 37 | 30026 / 40026 Bit 12 | FD01 Bit 12 | FD01 Bit 12 | FD01 Bit 12 | FD01 Bit 12 | FD01 Bit 12 | N/A
Standby ST=On | Digital Input |  |  | R | BI9 | BI9 | 38 | 30026 / 40026 Bit 13 | FD01 Bit 13 | FD01 Bit 13 | FD01 Bit 13 | FD01 Bit 13 | FD01 Bit 13 | N/A
Standby | Digital Input |  |  | R | BI10 | BI10 | 39 | 30026 / 40026 Bit 14 | FD01 Bit 14 | FD01 Bit 14 | FD01 Bit 14 | FD01 Bit 14 | FD01 Bit 14 | N/A
Hand/Auto | Digital Input |  |  | R | BI11 | BI11 | 40 | 30026 / 40026 Bit 15 | FD01 Bit 15 | N/A | N/A | N/A | N/A | N/A
Control Status | Digital Input |  |  | R | BI12 | BI12 | 41 | 30027 / 40027 Bit 0 | FD42 Bit 0 | N/A | N/A | FD42 Bit 0 | FD42 Bit 0 | N/A
KWH Counting | Digital Input |  |  | R | BI13 | BI13 | 42 | 30027 / 40027 Bit 1 | FD42 Bit 1 | FD42 Bit 1 | N/A | FD42 Bit 1 | FD42 Bit 1 | N/A
Heartbeat | Digital Input |  |  | R | BI14 | BI14 | 43 | 30028 / 40028 Bit 11 | FD49 Bit 11 | FD49 Bit 11 | FD49 Bit 11 | N/A | N/A | N/A
F Terminal | Digital Input |  |  | R | BI15 | BI15 | 44 | 30029 / 40029 Bit 0 | FD06 Bit 0 | FD06 Bit 0 | FD06 Bit 0 | FD06 Bit 0 | FD06 Bit 0 | FE06 Bit 0
R Terminal | Digital Input |  |  | R | BI16 | BI16 | 45 | 30029 / 40029 Bit 1 | FD06 Bit 1 | FD06 Bit 1 | FD06 Bit 1 | FD06 Bit 1 | FD06 Bit 1 | FE06 Bit 1
ST Terminal | Digital Input |  |  | R | BI17 | BI17 | 46 | 30029 / 40029 Bit 2 | N/A | N/A | N/A | FD06 Bit 2 | FD06 Bit 2 | FE06 Bit 2
RES Terminal | Digital Input |  |  | R | BI18 | BI18 | 47 | 30029 / 40029 Bit * | FD06 Bit 2 | FD06 Bit 2 | N/A | FD06 Bit 3 | FD06 Bit 3 | FE06 Bit 3
S1 Terminal | Digital Input |  |  | R | BI19 | BI19 | 48 | 30029 / 40029 Bit * | FD06 Bit 3 | FD06 Bit 3 | FD06 Bit 2 | FD06 Bit 4 | FD06 Bit 4 | FE06 Bit 4
S2 Terminal | Digital Input |  |  | R | BI20 | BI20 | 49 | 30029 / 40029 Bit * | FD06 Bit 4 | FD06 Bit 4 | FD06 Bit 3 | FD06 Bit 5 | FD06 Bit 5 | FE06 Bit 5
S3 Terminal | Digital Input |  |  | R | BI21 | BI21 | 50 | 30029 / 40029 Bit * | FD06 Bit 5 | FD06 Bit 5 | N/A | FD06 Bit 6 | FD06 Bit 6 | FE06 Bit 6
S4 Terminal | Digital Input |  |  | R | BI22 | BI22 | 51 | 30029 / 40029 Bit * | FD06 Bit 6 | N/A | N/A | FD06 Bit 7 | FD06 Bit 7 | FE06 Bit 7
S5 Terminal | Digital Input |  |  | R | BI23 | BI23 | 52 | 30029 / 40029 Bit 7 | FD06 Bit 7 | N/A | N/A | N/A | N/A | N/A
R1 Terminal | Digital Input |  |  | R | BI24 | BI24 | 53 | 30030 / 40030 Bit 3 | FD07 Bit 3 | N/A | N/A | N/A | N/A | N/A
R2 Terminal | Digital Input |  |  | R | BI25 | BI25 | 54 | 30030 / 40030 Bit 4 | FD07 Bit 4 | N/A | N/A | N/A | N/A | N/A
OUT1 Terminal | Digital Input |  |  | R | BI24 | BI24 | 53 | 30030 / 40030 Bit 0 | N/A | N/A | N/A | FD07 Bit 0 | FD07 Bit 0 | FE07 Bit 0
OUT2 Terminal | Digital Input |  |  | R | BI25 | BI25 | 54 | 30030 / 40030 Bit 1 | N/A | N/A | N/A | FD07 Bit 1 | FD07 Bit 1 | FE07 Bit 1
RY/RC Terminal | Digital Input |  |  | R | BI24 | BI24 | 53 | 30030 / 40030 Bit 0 | N/A | FD07 Bit 0 | N/A | N/A | N/A | N/A
OUT Terminal | Digital Input |  |  | R | BI25 | BI25 | 54 | 30030 / 40030 Bit * | N/A | FD07 Bit 1 | FD07 Bit 0 | N/A | N/A | N/A
FL Terminal | Digital Input |  |  | R | BI26 | BI26 | 55 | 30030 / 40030 Bit 2 | FD07 Bit 2 | FD07 Bit 2 | FD07 Bit 2 | FD07 Bit 2 | FD07 Bit 2 | FE07 Bit 2
FP Terminal | Digital Input |  |  | R | BI27 | BI27 | 56 | 30030 / 40030 Bit 1 | FD07 Bit 1 | N/A | N/A | N/A | N/A | N/A
ASD Com Error | Digital Input |  |  | R | BI28 | BI28 | 57 | 30056 / 40056 | RED-485 Param | RED-485 Param | RED-485 Param | RED-485 Param | RED-485 Param | RED-485 Param
Frequency Command | Analog Output | 0.01 | Hz | R/W | AO1 | AO1 | 60 | 40100 | FA05 | FA01 | FA01 | FA01 | FA05 | FA05
Speed Command | Analog Output | 1 | RPM | R/W | AO2 | AO2 | 61 | 40101 | FA19 | FA13 | N/A | FA13 | FA13 | N/A
Torque Command | Analog Output | 0.01 | % | R/W | AO3 | AO3 | 62 | 40102 | FA32 | N/A | N/A | FA32 | FA32 | FA32
Acceleration Time 1 | Analog Output | 0.1 | Seconds | R/W | AO4 | AO4 | 63 | 40103 | 9 | 9 | 9 | 9 | 9 | 9
Deceleration Time 1 | Analog Output | 0.1 | Seconds | R/W | AO5 | AO5 | 64 | 40104 | 10 | 10 | 10 | 10 | 10 | 10
FM Terminal Command | Analog Output | 0.01 | % | R/W | AO6 | AO6 | 65 | 40105 | FA51 | FA51 | FA51 | FA51 | FA51 | N/A
AM Terminal Command | Analog Output | 0.01 | % | R/W | AO7 | AO7 | 66 | 40106 | FA52 | N/A | N/A | FA52 | FA52 | N/A
Analog Output Data Command | Analog Output | 0.01 | % | R/W | AO6 | AO6 | 65 | 40105 | N/A | N/A | N/A | N/A | N/A | FA51
Run/Stop Command | Digital Output |  |  | R/W | BO1 | BO1 | 70 | 40107 Bit 10 | FA04 Bit 10 | FA00 Bit 10 | FA00 Bit 10 | FA00 Bit 10 | FA04 Bit 10 | FA04 Bit 10
Forward/Reverse Command | Digital Output |  |  | R/W | BO2 | BO2 | 71 | 40107 Bit 9 | FA04 Bit 9 | FA00 Bit 9 | FA00 Bit 9 | FA00 Bit 9 | FA04 Bit 9 | FA04 Bit 9
Fault Reset | Digital Output |  |  | R/W | BO3 | BO3 | 72 | 40107 Bit 13 | FA04 Bit 13 | FA00 Bit 13 | FA00 Bit 13 | FA00 Bit 13 | FA04 Bit 13 | FA04 Bit 13
DC Brake Command | Digital Output |  |  | R/W | BO4 | BO4 | 73 | 40107 Bit 7 | FA04 Bit 7 | FA00 Bit 7 | FA00 Bit 7 | FA00 Bit 7 | FA04 Bit 7 | FA04 Bit 7
Jog Run Command | Digital Output |  |  | R/W | BO5 | BO5 | 74 | 40107 Bit 8 | FA04 Bit 8 | FA00 Bit 8 | FA00 Bit 8 | FA00 Bit 8 | FA04 Bit 8 | FA04 Bit 8
Coast Stop Command | Digital Output |  |  | R/W | BO6 | BO6 | 75 | 40107 Bit 11 | FA04 Bit 11 | FA00 Bit 11 | FA00 Bit 11 | FA00 Bit 11 | FA04 Bit 11 | N/A
Free Run Command | Digital Output |  |  | R/W | BO6 | BO6 | 75 | 40107 Bit 11 | N/A | N/A | N/A | N/A | N/A | FA04 Bit 11
Emergency Stop Command | Digital Output |  |  | R/W | BO7 | BO7 | 76 | 40107 Bit 12 | FA04 Bit 12 | FA00 Bit 12 | FA00 Bit 12 | FA00 Bit 12 | FA04 Bit 12 | FA04 Bit 12
Frequency Priority | Digital Output |  |  | R/W | BO8 | BO8 | 77 | 40107 Bit 14 | FA04 Bit 14 | FA00 Bit 14 | FA00 Bit 14 | FA00 Bit 14 | FA04 Bit 14 | FA04 Bit 14
Command Priority | Digital Output |  |  | R/W | BO9 | BO9 | 78 | 40107 Bit 15 | FA04 Bit 15 | FA00 Bit 15 | FA00 Bit 15 | FA00 Bit 15 | FA04 Bit 15 | FA04 Bit 15
Preset Speed 1 | Digital Output |  |  | R/W | BO10 | BO10 | 79 | 40107 Bit 0 | FA04 Bit 0 | FA00 Bit 0 | FA00 Bit 0 | FA00 Bit 0 | FA04 Bit 0 | FA04 Bit 0
Preset Speed 2 | Digital Output |  |  | R/W | BO11 | BO11 | 80 | 40107 Bit 1 | FA04 Bit 1 | FA00 Bit 1 | FA00 Bit 1 | FA00 Bit 1 | FA04 Bit 1 | FA04 Bit 1
Preset Speed 3 | Digital Output |  |  | R/W | BO12 | BO12 | 81 | 40107 Bit 2 | FA04 Bit 2 | FA00 Bit 2 | FA00 Bit 2 | FA00 Bit 2 | FA04 Bit 2 | FA04 Bit 2
Preset Speed 4 | Digital Output |  |  | R/W | BO13 | BO13 | 82 | 40107 Bit 3 | FA04 Bit 3 | FA00 Bit 3 | FA00 Bit 3 | FA00 Bit 3 | FA04 Bit 3 | FA04 Bit 3
Hand/Auto Selection | Digital Output |  |  | R/W | BO14 | BO14 | 83 | 40108 Bit 0 | FA08 Bit 0 | N/A | N/A | N/A | N/A | N/A
Local/Remote Selection | Digital Output |  |  | R/W | BO14 | BO14 | 83 | 40108 Bit 0 | N/A | FA08 Bit 0 | N/A | N/A | N/A | N/A
Control Switching | Digital Output |  |  | R/W | BO15 | BO15 | 84 | 40109 Bit 0 | FA22 Bit 0 | N/A | N/A | FA22 Bit 0 | FA22 Bit 0 | FA22 Bit 0
Reset KWH | Digital Output |  |  | R/W | BO16 | BO16 | 85 | 40109 Bit 1 | FA22 Bit 1 | FA20 Bit 1 | N/A | FA22 Bit 1 | FA22 Bit 1 | N/A
Data Bit 0 | Digital Output |  |  | R/W | BO17 | BO17 | 86 | 40110 Bit 0 | FA50 Bit 0 | N/A | N/A | N/A | N/A | N/A
Data Bit 1 | Digital Output |  |  | R/W | BO18 | BO18 | 87 | 40110 Bit 1 | FA50 Bit 1 | N/A | N/A | N/A | N/A | N/A
Data Output 1 | Digital Output |  |  | R/W | BO17 | BO17 | 86 | 40110 Bit 0 | N/A | FA50 Bit 0 | FA50 Bit 0 | FA50 Bit 0 | FA50 Bit 0 | FA50 Bit 0
Data Output 2 | Digital Output |  |  | R/W | BO18 | BO18 | 87 | 40110 Bit 1 | N/A | FA50 Bit 1 | N/A | FA50 Bit 1 | FA50 Bit 1 | FA50 Bit 1
Data Output 3 | Digital Output |  |  | R/W | BO19 | BO19 | 88 | 40110 Bit 2 | N/A | N/A | N/A | FA50 Bit 2 | FA50 Bit 2 | FA50 Bit 2
Data Output 4 | Digital Output |  |  | R/W | BO20 | BO20 | 89 | 40110 Bit 3 | N/A | N/A | N/A | FA50 Bit 3 | FA50 Bit 3 | FA50 Bit 3
Data Output 5 | Digital Output |  |  | R/W | BO21 | BO21 | 90 | 40110 Bit 4 | N/A | N/A | N/A | FA50 Bit 4 | FA50 Bit 4 | FA50 Bit 4
Data Output 6 | Digital Output |  |  | R/W | BO22 | BO22 | 91 | 40110 Bit 5 | N/A | N/A | N/A | FA50 Bit 5 | FA50 Bit 5 | FA50 Bit 5
Data Output 7 | Digital Output |  |  | R/W | BO23 | BO23 | 92 | 40110 Bit 6 | N/A | N/A | N/A | FA50 Bit 6 | FA50 Bit 6 | FA50 Bit 6